## Dark Roof
Air Temperature | 303 | K | 30 | C | 86 | F
Incoming Solar Radiation | 800 | W/m2
Sky Temperature | 293 | K | a clear sky has a radiation temp of about 10 below ambient, maybe more | [7 empty] | 22
Interior Temperature | 323 | K | 50
Emmitance (lw) | 0.9
Absorptance (sw) | 0.9
Roof Resistance | 3 | RSI | 17.034 | R
[8 empty] | 1 | 354.3 | 3.2
[7 empty] | RSI | 3.5 | 356.8
Surface Temperature | 354.0384 | K | 81.0384 | C | 177.8692 | F |  | 10 | 357.5 | 0.7
| Solar Increase (roughly sol-air temp) |  | 51.0384 | C | 123.8692 | F
Gains
Longwave | 376.0937 | W/m2
Shortwave | 720 | W/m2
Total | 1096.0937 | W/m2
Losses |  |  |  |  | Coefficient
Convection | 284.0189 | W/m2 |  |  | 5.5648 | W/m2
Conduction | 10.3461 | W/m2 |  |  | 0.20271 | W/m2
Radiation | 801.7284 | W/m2 |  |  | 15.7083 | W/m2
Total | 1096.0934 | W/m2 |  |  | 21.4758 | W/m2
Difference | 0.00030132 | use Goal Seek to set to zero
[8 empty] | 396000 | J/K
440
7.3333

## White high E
Air Temperature | 293 | K | 20 | C | 68 | F
Incoming Solar Radiation | 1000 | W/m2
Sky Temperature | 283 | K | a clear sky has a radiation temp of about 10 below ambient, maybe more
White painted alu - fresh and clean
Emmitance (lw) | 0.9 | normal materials
Absorptance (sw) | 0.2 | a clean white value
Surface Temperature | 309.1245 | K | 36.1245 | C | 97.024 | F
| Solar Increase (roughly sol-air temp) |  | 16.1245 | C | 61.024 | F
Gains
Longwave | 327.3191 | W/m2
Shortwave | 200 | W/m2
Total | 527.3191 | W/m2
Losses |  |  |  |  | Coefficient
Convection | 61.3478 | W/m2 |  |  | 3.8046 | W/m2
Radiation | 465.9712 | W/m2 |  |  | 28.8984 | W/m2
Total | 527.3191 | W/m2 |  |  | 32.703 | W/m2
Difference | -4.4876e-07 | use Goal Seek to set to zero

## Galv Steel
Air Temperature | 293 | K | 20 | C | 68 | F
Incoming Solar Radiation | 1000 | W/m2 |  |  |  |  | 949.9
Sky Temperature | 283 | K | a clear sky has a radiation temp of about 10 below ambient, maybe more
Emmitance (lw) | 0.2 | new zinc roof
Absorptance (sw) | 0.65 | typical zinc value
Surface Temperature | 371.796 | K | 98.796 | C | 209.8328 | F
| Solar Increase (roughly sol-air temp) |  | 78.796 | C | 173.8328 | F
Gains
Longwave | 72.7376 | W/m2
Shortwave | 650 | W/m2
Total | 722.7376 | W/m2
Losses |  |  |  |  | Coefficient
Convection | 506.051 | W/m2 |  |  | 6.4223 | W/m2
Radiation | 216.6866 | W/m2 |  |  | 2.75 | W/m2
Total | 722.7375 | W/m2 |  |  | 9.1723 | W/m2
0.070866
Difference | 5.3961e-05 | use Goal Seek to set to zero

## White LowE roof
Air Temperature | 293 | K | 20 | C | 68 | F
Incoming Solar Radiation | 1000 | W/m2 |  |  |  |  | 949.9
Sky Temperature | 283 | K | a clear sky has a radiation temp of about 10 below ambient, maybe more
Emmitance (lw) | 0.05 | polished aluminum
Absorptance (sw) | 0.15 | polished aluminum
Surface Temperature | 327.704 | K | 54.704 | C | 130.4672 | F
| Solar Increase (roughly sol-air temp) |  | 34.704 | C | 94.4672 | F
Gains
Longwave | 18.1844 | W/m2
Shortwave | 150 | W/m2
Total | 168.1844 | W/m2
Losses |  |  |  |  | Coefficient
Convection | 170.0389 | W/m2 |  |  | 4.8997 | W/m2
Radiation | 32.6949 | W/m2 |  |  | 0.94211 | W/m2
Total | 202.7338 | W/m2 |  |  | 5.8418 | W/m2
0.025677
Difference | -34.5494 | use Goal Seek to set to zero

## Green LowE roof
Air Temperature | 293 | K | 20 | C | 68 | F
Incoming Solar Radiation | 1000 | W/m2 |  |  |  |  | 949.9
Sky Temperature | 283 | K | a clear sky has a radiation temp of about 10 below ambient, maybe more
Emmitance (lw) | 0.1 | a special low-E coating
Absorptance (sw) | 0.5 | a light green metal roof
Surface Temperature | 363.5993 | K | 90.5993 | C | 195.0787 | F
| Solar Increase (roughly sol-air temp) |  | 70.5993 | C | 159.0787 | F
Gains
Longwave | 36.3688 | W/m2
Shortwave | 500 | W/m2
Total | 536.3688 | W/m2
Losses |  |  |  |  | Coefficient
Convection | 437.2684 | W/m2 |  |  | 6.1937 | W/m2
Radiation | 99.1004 | W/m2 |  |  | 1.4037 | W/m2
Total | 536.3688 | W/m2 |  |  | 7.5974 | W/m2
0.065812
Difference | -5.2394e-06 | use Goal Seek to set to zero